## Confidentiality
Reliable Addition of Large Datacentric Loads
Interconnection Request Data Questionnaire
General Information
Version: 2.0
Document ID: 1844a
Approval Date: 09/17/2026
Open Distribution
Copyright © 2026 North American Transmission Forum (“NATF”). All rights reserved. Not for sale or commercial use. The NATF makes no and hereby disclaims all representations or warranties, either express or implied, relating to the content, including as to the accuracy or completeness of the information. No liability is assumed by the NATF for any damages arising directly or indirectly from the content or by the use or application thereof. Use of the content constitutes agreement to defend, indemnify, and hold the NATF harmless from and against all claims arising from such use.

## Workbook Instructions
Instructions for use
This Excel workbook, “NATF RALDL Interconnection Request Data Questionnaire - General Information” and its companion workbook for technical data serve as appendices to the NATF RALDL Interconnection Requests and Studies practice document. This workbook contains templates for collecting information from interconnection customers as specificed in the parent practice document.
Customizing the Questionnaire
Not all data fields may be appropriate for all users and situations. The user must verify that data requested in the questionnaire matches their particular interconnection requirements if they did not adopt the NATF practices in total. In addition, worksheets within this workbook may be moved to the companion technical data workbook if better suited to interconnection process flow.
Cells with light green fill indicate information to be entered by the interconnection customer.
Cells with light blue fill are questions for consideration by the interconnection customer.
Cells with gray fill are linked to the General Information tab for continuity across all worksheets.

## General Information
Large Datacentric Load Questionnaire
General Information
Instructions: Please fill-in the GREEN highlighted areas on this page; more instructions below
Requestor Information: | Company Name | ____
| Project Name | ____
| Project Location | ____
| Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Owner Information (if not Requestor): | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Tenant Information (if applicable): | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Data Center Information: | Type | ____
| Anticipated Peak Load (MW) | ____
Technical Lead on Data and Models: | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Dates and Schedule: | Initial Request | ____
| Date of Site Control | ____
| Questionnaire Completed | ____
| Desired In-service Date | ____
Objective:
Detailed data for large datacentric loads is essential for evaluation of the interconnection to commence. Interconnection requests must include a wide range of general information about the interconnection customer, site, and technical data about the nature of the load and potential on-site generation, batteries, uninterruptible power supply (UPS) systems, on-site resources, and load models for adequate interconnection evaluations to occur. Accurate and complete data submittals lead to better interconnection studies and (potentially) a faster interconnection process.

## Ant. Aggregate Facilty Demand
Large Datacentric Load Questionnaire
Anticipated Aggregate Facilty Demand
Company Name | ____ |  |  | Type or Use | ____
Project Name | ____ |  |  | Initial Request | ____
Project Location | ____ |  |  | Energization Date | ____
Objective:
Require the interconnection customer to communicate the planned project schedule for load over time by providing maximum anticipated aggregate facility demand on a seasonal basis in MVA with power factor for the first five years. This should also include overall peak anticipated demand over the first 10 years of interconnection and a forecast for seasonal demand for year 15.
|  | Summer Peak Demand |  | Winter Peak Demand |  | Light Load
Year | Calendar Year | MVA | Power Factor | MVA | Power Factor | MVA | Power Factor
Year 0 (Initial Load)
Year 1
Year 2
Year 3
Year 4
Year 5
Highest peak in first 10 years
Year 15
What is the most severe demand contingency, i.e., how much load is removed from the transmission grid
following the worst single contingency in the data center facility?
Will the data center be operated in coordination with other data centers on the same transmission network?
If so, then provide load profile details of all impacted data centers.

## Load Behavior and Flexibility
Large Datacentric Load Questionnaire
Detailed Load Behavior and Operational Flexibility
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Require the interconnection customer to communicate as much information as possible about the data center operational load behavior to those responsible for interconnection evaluations. including how the demand of the data center facility changes over time for normal and abnormal operation. The flexibility of large loads may also have significant implications on interconnection studies and processes ranging from equivalent treatment as firm load on one hand, to a fully dispatchable load that can rapidly follow dispatch commands on the other. Load profile and flexibility should be described in detail by providing the following information:
Provide max ramp over one second duration (MW/s) in both directions during normal operation:
Provide max ramp over one minute duration (MW/min) in both directions during normal operation:
Describe how electricity prices influence facilty demand:
Describe how data center on-site backup generation (if applicable) is intended to be operated in relation
to the transmission grid (e.g., full backup or partial backup when disconnected).
Describe how the facility can modify its demand to meet an externally provided objective:
Can the facility curtail demand in a controlled manner:
Can the facility increase demand in a controlled manner (e.g., after curtailment or for restoration):
Describe how the facility demand can be scheduled or forecasted in advance and over what time horizon
(hours, days, or months):
Describe what mechanism(s) is/are employed by the load to control its demand.
Disconnection of load, either in blocks, or on an entire plant basis:
Direct control of loads, e.g. dynamic power targets for compute loads:
On-site energy storage to offset or increase net load demand
On-site generation that can be dispatched to offset net load demand
Describe what constraints exist that affect the degree to which a load’s demand can be modified in terms of
minimum consumption level in MW (i.e., describe what portion of demand is fixed):
Describe the expected response time between receipt of the request/command to modify the load’s demand and
the load’s demand meeting that request/command:
MW response within 5 minutes, 30 minutes, 60 minutes, etc.
Specify differences in response for local vs central dispatch controls
Specify the facility capability to receive and follow electronic dispatch commands:
Set consumption to X MW
Consume no more than Y MW
Consume at least Z MW
If the load is one of several loads managed by the same entity, specify whether demand curtailed at one load within
the interconnecting authority’s footprint would affect the consumption of the other loads managed by the entity
(i.e., will demand be shifted from one load to another load)?

## Prelim One-Line
Large Datacentric Load Questionnaire
Preliminary One-Line Diagram
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
An electrical one line for a large load facility should clearly show how power enters the site; how it is transformed, protected, distributed, and backed up; and how redundancy is achieved. The purpose is to give planners and engineers an accurate, non intrusive, non proprietary view of device configurations, load paths, protection boundaries, and the facility’s behavior during faults, switching events, and contingencies. A concise but complete one line supports system reliability, proper fault current coordination, voltage stability, and predictable behavior during load transfers or emergency operations. Require the interconnection customer to provide the following data in a one-line diagram:
Point of interconnection (POI), bus configuration, and ownership demarcation to clearly show where utility power enters and how faults will be isolated.
Main transformers with ratings (MW and MVAR), impedance, tap settings, and grounding method, since these define fault levels, voltage regulation, and system behavior under load.
On site generation, parallelling/switching mode, and interlocks, which govern load transfer behavior and fault contributions.
Advanced technologies such as static synchronous compensators or other FACTS devices, when applicable.
Battery energy storage systems with an indication of whether advanced inverter functions (e.g., grid forming) are enabled.
Redundant distribution paths and tie-breaker logic, showing how the data center maintains service during N-1 events and how load transfers occur.
Uninterruptible power supplies, transfer switches (automatic and static), harmonic producing equipment, and any filtering, since these affect transient behavior and power quality.
Protection zones, breaker locations, metering, and current and potential transformer placement to illustrate how faults are detected and cleared without impacting adjacent systems.
Differentiation of central plant loads (cooling), lighting, and process/computational loads (e.g. GPUs).
Transformation and voltage levels across tiers of distribution.
Insert screen-shot of One-Line Diagram here for context and submit native file separately.