## Confidentiality
Reliable Addition of Large Datacentric Loads
Interconnection Request Data Questionnaire
Technical Information
Version: 2.0
Document ID: 1844b
Approval Date: 09/17/2026
Open Distribution
Copyright © 2026 North American Transmission Forum (“NATF”). All rights reserved. Not for sale or commercial use. The NATF makes no and hereby disclaims all representations or warranties, either express or implied, relating to the content, including as to the accuracy or completeness of the information. No liability is assumed by the NATF for any damages arising directly or indirectly from the content or by the use or application thereof. Use of the content constitutes agreement to defend, indemnify, and hold the NATF harmless from and against all claims arising from such use.

## Workbook Instructions
Instructions for use
This Excel workbook, “NATF RALDL Interconnection Request Data Questionnaire - Technical Information” and its companion workbook for general information serve as appendices to the NATF RALDL Interconnection Requests and Studies practice document. This workbook contains templates for collecting information from interconnection customers as specificed in the parent practice document.
Customizing the Questionnaire
All data fields may not be appropriate for all users and situations. The user must verify that data requested in the questionnaire matches their particular interconnection requirements if they did not adopt the NATF practices in total. In addition, worksheets within this workbook may be moved to the companion general information workbook if better suited to interconnection process flow.
Cells with light green fill indicate information to be entered by the interconnection customer.
Cells with light blue fill are questions for consideration by the interconnection customer.
Cells with gray fill are linked to the General Information tab for continuity across all worksheets.

## General Information
Large Datacentric Load Questionnaire
General Information
Instructions: Please fill-in the GREEN highlighted areas on this page, more instructions below
Requestor Information: | Company Name | ____
| Project Name | ____
| Project Location | ____
| Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Owner Information (if not Requestor): | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Tenant Information (if applicable): | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Data Center Information: | Type | ____
| Anticipated Peak Load (MW) | ____
Technical Lead on Data and Models: | Point of Contact | ____
| Title | ____
| Phone Number | ____
| Email | ____
Dates and Schedule: | Initial Request | ____
| Date of Site Control | ____
| Questionnaire Completed | ____
| Desired In-service Date | ____
Objective:
Detailed data for large datacentric loads is essential for evaluation of the interconnection to commence. Interconnection requests must include a wide range of general information about the interconnection customer, site, and technical data about the nature of the load and potential on-site generation, batteries, uninterruptible power supply (UPS) systems, on-site resources, and load models for adequate interconnection evaluations to occur. Accurate and complete data submittals lead to better interconnection studies and (potentially) a faster interconnection process.

## Load Components by Type
Large Datacentric Load Questionnaire
Load Components by Type
Company Name | ____ |  | Type or Use | ____
Project Name | ____ |  | Initial Request | ____
Project Location | ____ |  | Energization Date | ____
Objective:
Large data center facilities represent complex, highly concentrated electrical loads with stringent requirements for reliability, power quality, redundancy, and scalability. Unlike conventional commercial or industrial facilities, data centers combine large continuous electronic loads with significant supporting mechanical and power-conditioning infrastructure. Major categories of loads typically present in a hyperscale or large enterprise data center include information technology (servers, storage, network hardware, etc.), lighting, power conditioning and distribution, cooling, and other auxiliary loads which support the balance of plant.
Provide the percentage breakdown of total MW consumption by the following components:
Computing / server load
Lighting load
Power distribution losses
Cooling load
Other auxiliary loads
Provide the percentage of the total facility load (MW) that is IT equipment during each season of build-out:
Year 0 (Initial Load)
Year 1
Year 2
Year 3
Year 4
Year 5
Highest peak in first 10 years
Year 15
Specify if the data center has a forced cooling system and, if so, identify the type:
Computer Room Air Conditioners (CRACs) with internal compressors
Computer Room Air Handlers (CRAHs) supplied with chilled water
Air-Handling Units (AHUs) dedicated to data center space
Direct liquid cooling (to chip or rack level)
Other (specify)
Identify how the motor components of the cooling system are driven:
Single-speed AC directly connected |  | Single-speed AC directly connected
Variable Frequency Drive (VFD) / inverter controlled |  | Single-speed AC directly connected
Other (specify) |  | Single-speed AC directly connected
Identify the Power Usage Effectiveness (PUE) target at full build-out
List the characteristics and MW (or %) of large motor loads (>=100 hp) - type, quantity, and starting method
List the characteristics and MW (or %) of small motor loads (<100 hp) - type, quantity, and drive type
Specify the transformer characteristics:
Nameplate rating (MVA) |  | Single-speed AC directly connected
Voltage ratio (primary / secondary) |  | Single-speed AC directly connected
Impedance (%Z) |  | Single-speed AC directly connected
Tap changer type (OLTC, NLTC, or fixed) |  | Single-speed AC directly connected
Configuration (Delta–Wye, Wye–Delta–Wye, or other) |  | Single-speed AC directly connected
Impedance (%Z) |  | Single-speed AC directly connected
Provide transformer test reports with saturation characteristics for all transformers, as soon as available.
Provide the expected inrush current magnitude and duration during initial energization and cold-start scenarios:
Identify the planned redundancy configuration (e.g., N+1, 2N, 2N+1) for the electrical distribution system:
Identify the required service reliability (e.g., Tier I, II, III, or IV per Uptime Institute):
Identify the availability requirements (% uptime):
Provide the level of requested redundancy in terms of dual or multiple utility feeds and describe
the preferred configuration (simultaneous, standby, etc.).

## Composite Load Model
Large Datacentric Load Questionnaire
Composite Load Model
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Provide key components for composite load model with percentage breakdown by load type.
Figure source: M. Saravanan, "ISO New England Composite Load Model: High-Level Overview, Benefits, Transition Roadmap and RFP Focus," [Online]. Available: https://www.iso-ne.com/static-assets/documents/100020/a07_2025_02_26_pac_composite_load_model.pdf.
Item | Description |  |  | Percentage
Motor A | Percentage of load consisting of three-phase induction motors with low inertia (H=0.1 sec) driving constant torque loads. These motors are found in commercial/industrial air conditioning compressors and refrigeration systems (not NEMA B). |  |  | %
Smaller 5–15 HP compressor motors typical of rooftop air conditioning units commonly found at grocery stores, consumer products stores, and malls.
Larger 200–500 HP compressor motors are typical of large commercial buildings’ central cooling systems
Motor B | Percentage of load consisting of three-phase induction motors with high inertia (H=0.25–0.10 sec) driving loads whose torque is proportional to speed squared. These motors are found in commercial ventilation fans and air-handling systems. |  |  | %
5–25 HP fan motors, which are normally NEMA B motors.
Motor C | Percentage of load consisting of three-phase induction motors with low inertia (H=0.1–0.2 sec). This represents motors commonly found in commercial water circulation pumps in central cooling systems. |  |  | %
5–25 HP pump motors, which are normally NEMA B motors.
Motor D | Percentage of load consisting of single-phase air conditioners. This represents commonly found residential single-phase air conditioners. |  |  | %
Electronic Load | Percentage of load consisting of power electronic converters. These are constant active and reactive power loads. |  |  | %
Static Load | Percentage of load that will be static. This represents incandescent lighting and all other loads whose behavior changes with voltage magnitude. |  |  | %
Table Source: Georgia Transmission Company, "Large Load Technical Data Sheet," 2025. [Online]. Available: https://www.oasis.oati.com/woa/docs/GTC/GTCdocs/Large_Load_Technical_Data_Sheet_11-1-25.pdf.

## PERC1 or ISO-NE Model
Large Datacentric Load Questionnaire
PERC1 or ISO-NE Model
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Provide ceasing and reconnection timing to populate PERC1 and/or ISO-NE UDM models.
Figure Source: PowerWorld Corporation, "Transient Models - Load Characteristic Model: PERC1," 2025. [Online]. Available: https://www.powerworld.com/WebHelp/Content/TransientModels_HTML/Load%20Characteristic%20PERC1.htm.
Item | Description |  |  | Percentage
Fcease | Fraction that will cease (between 0 and 1)
Vcease | Voltage threshold for cease logic [per unit]
Tcease | Time delay for cease logic to be initiated for (>= 0) [seconds]
Vrecon | Voltage threshold to initiate power ramp reconnection logic (Vrecon >= Vcease) [per unit]
Trecon | Time delay for ramp up logic to be initiated (>= 0) [seconds]
Tramp | Ramp up time (>= 0) [seconds]
Frecon | Of the Fraction that ceases, this is the fraction that then reconnects (between 0 and 1)t]
Table Source: PowerWorld Corporation, "Transient Models - Load Characteristic Model: PERC1," 2025. [Online]. Available: https://www.powerworld.com/WebHelp/Content/TransientModels_HTML/Load%20Characteristic%20PERC1.htm.

## Reactive Devices
Large Datacentric Load Questionnaire
Reactive Devices
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Data centers can have large inductive and power electronic loads, which can significantly influence the stability of the grid, and some facilities may employ active power factor correction onsite. Require the interconnection customer to provide the following information:
Device nameplate specifications for all reactive devices at the facility:
Purpose of reactive devices and control objective:
Specify whether reactive components are fixed or variable:
Anticipated real-time and historical reactive power demand based on comparable facilities:
Anticipated instantaneous power factor and whether any power factor correction equipment will be utilized:
Specifications for reactive devices that will be configured as harmonic filters including filter type,
tuning frequencies, and control methodology:
Power factor correction methods to address dynamic operational changes from datacentric loads:

## Short-Circuit Ratings
Large Datacentric Load Questionnaire
Short Circuit Ratings
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Data centers have sensitive electronics and may include onsite generation. Understanding how the facility may impact the grid and any grid strength requirements is important for completing interconnection assessments. Require the interconnection customer to provide the following information to identify the short circuit impacts on the Point of Interconnection (POI) and allow study of the ability of the system to serve the load reliably:
Connecting transformer configuration:
Data for each backup generator (energy storage) on the customer side of the POI including, size,
impedance, and type (inverter based, synchronous, etc.):
Whether backup generators will ever run in parallel with the connected utility system:
Information on required minimum grid strength in terms of short circuit ratio (SCR) needed for data center operations:
Note: During the interconnection study, the utility will identify the maximum fault current availability of the planned interconnection as well as minimum N-1 fault current availability. The interconnection customer is expected to ensure its equipment is rated to withstand the provided maximum fault duty including a margin for system growth.

## Power Quality
Large Datacentric Load Questionnaire
Power Quality
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Large datacentric loads will be subject to analysis demonstrating that they will not adversely impact the power quality of the electrical system. In general, objectionable power quality impacts are not expected when analysis indicates power quality requirements will be satisfied. Require the customer to provide the following basic technical planning data required to be submitted to evaluate the load with respect to harmonic distortion, voltage fluctuations and associated light flicker, rapid voltage change, voltage unbalance, and voltage and frequency variation ride through performance.
Expected facility harmonic current injection spectrum, up to the 50th harmonic order, aggregated at
the reference point of applicability:
Expected magnitude and frequency of variations in active and reactive power, aggregated at the reference
point of applicability:

## Voltage Performance
Large Datacentric Load Questionnaire
Voltage Performance
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Voltage performance under various system conditions must be specified and understood to evaluate interconnection requests effectively. Require the following voltage performance information including reconnection times to align with performance requirements such as ride-through:
Voltage sag level/duration at which the predominant load (computer/server loads) disconnects from the utility system:
Voltage sag level/duration at which the cooling load disconnects from the utility system:
Measurement method (per phase or three-phase RMS) for voltage sag levels used for disconnection:
Voltage swell level/duration at which the predominant load (computer/server loads) disconnects from the utility system:
Voltage swell level/duration at which the cooling load disconnects from the utility system:
Measurement method (per phase or three-phase RMS) for voltage swell levels used for disconnection:
Threshold number of voltage disturbances used to determine disconnection from the utility system:

## Frequency Performance
Large Datacentric Load Questionnaire
Frequency Performance
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Similarly, frequency performance under various system conditions must be specified and understood to evaluate interconnection requests effectively. Require the following frequency performance information including reconnection times to align with performance requirements such as ride-through:
Frequency sag level/duration at which the predominant load (computer/server loads) disconnects from the utility system:
Frequency sag level/duration at which the cooling load disconnects from the utility system:
Frequency swell level/duration at which the predominant load (computer/server loads) disconnects from the utility system:
Frequency swell level/duration at which the cooling load disconnects from the utility system:

## UPS and Generation Data
Large Datacentric Load Questionnaire
UPS and Generation Data
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Since short-duration power disturbances can result in service outages, data corruption, or permanent equipment damage, UPS systems are also a fundamental component of data center electrical infrastructure. UPS systems protect data center loads from power interruptions, voltage sags/swells, frequency deviations, and waveform distortions, thereby ensuring continuity of operations and maintaining equipment reliability. Require the following information on datacenter UPS and backup generation:
Specify if the computational load has a UPS
If the computation load has a UPS, provide the following information:
Type(s) of UPS
UPS computational load
UPS capacity (MVA) and % of the facility load supported by UPS
UPS input power factor (based on measurement/ facility design or UPS parameter data)
Normal Operation mode of the data center IT load
IT/Computing load battery design back up time (in sec)
Explain the characteristics (manual or automatic) that lead to reconnection to the grid:
Time duration for load transfer to occur
UPS trip condition? (trip values and duration)
Is the UPS centralized, modular, or distributed (architecture)?
UPS redundancy configurations (N+1, 2N, 2(N+1))?
o N+1: one additional UPS to back up a single failure
o 2N: two completely independent UPS systems
o 2(N+1): fully redundant plus backup for each system
What is the size of the data center Emergency Generator (EG) and Battery Energy Storage Systems (BESS)
in relation to the data center load
Can the EG and BESS be dispatched to support the entire/partial load during system events?
If so, for how many hours?
Are periodic operational tests conducted that involve actual load transfer through the UPS system? If so, describe them:

## Battery Storage
Large Datacentric Load Questionnaire
Battery Storage
Company Name | ____ | Type or Use | ____
Project Name | ____ | Initial Request | ____
Project Location | ____ | Energization Date | ____
Objective:
Utility scale battery energy storage systems are mature technologies that provide longer duration services such as peak shaving, frequency regulation, and grid balancing to help maintain system reliability over broad geographic areas. These solutions operate from cycles to hours and support the stability of the electrical grid by smoothing large scale variability and enabling greater renewable integration. Inside facilities, battery storage operates in much the same way to mitigate the highly variable power profiles associated with datacentric workloads including emerging artificial intelligence learning modes in data centers. Rather than contributing to regional energy balancing, facility level batteries act within the plant to buffer fast transients, protect onsite generation, and maintain internal power quality. Battery storage should also be evaluated alongside other fast response technologies—such as STATCOMs—that provide voltage stabilization and reactive support, helping determine the most appropriate solution for a facility’s specific challenges.
Specify if the computational load has onsite battery storage
If the computation load has onsite battery storage, provide the following information:
Continuous/peak AC power (MW/MVA), duration (minutes/hours), and minimum/maximum state‑of‑charge constraints
aligned to operational scenarios.
Response‑time & ramp‑rate requirements including voltage droop settings:
Battery ride-through curves and settings:
Coordination and confirmation of protection setpoints between the facility and the utility including
over/under voltage/frequency trip points.
Short‑circuit & fault behavior: Expected fault current contribution (magnitude, duration).
Power quality limits and filtering needs: Harmonics, flicker, and any reactive power/voltage support setpoints.
PMU data including phasor angle/magnitude, voltage/current, frequency, timestamp resolution, sampling rate,
event capture for PQ data related to voltage sags, voltage transients, harmonics, and flicker.
Battery technology & life model: Chemistry (e.g., Li‑ion variant), cycle/depth‑of‑discharge profile, round‑trip efficiency,
calendar/cycle life expectations, and degradation assumptions used for sizing.
Safety, code, and compliance requirements including fire detection and suppression, gas detection/venting
and emergency protocol.
Controls objective and philosophy which includes integration with internal building management requirements and
interface with external SCADA and EMS systems, including system latency requirements.
Dispatch authority who sends state of charge, available capacity, and operating limits to support forecast-aligned,
dispatchable operation.
Sequencing with UPS and generators, which includes islanding requirements, when this will occur (such as number of faults)
and how system restoration occurs.
Cybersecurity attributes for all data and control pathways (authentication, encryption, role-based access,
secure interfaces, and audit logging).